## HIOReportOutput
Region | NSP | Start | Finish | Network Asset | Impact | Recall | Status | Status and Market Notice | Project Work? | Unplanned? | DNSP Aware? | Generator Aware? | Inter-Regional | Impact Region, Reason and Duration | Vs Old | Duration
TAS | TasNetworks | 2023-01-24 07:00 | 2023-01-24 14:30 | Gordon - Chapel St No.1 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  |  | T |  | TAS Maintenance 7.5 Hours | #REF! | 7.5 Hours
QLD | Powerlink | 2023-02-08 07:00 | 2023-02-08 17:00 | Nebo - Strathmore (822) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  | T |  |  | QLD Commissioning 10 Hours | #REF! | 10 Hours
TAS | TasNetworks | 2023-02-08 07:00 | 2023-02-08 14:30 | Gordon - Chapel St No.2 220 kV Line | <<NEW since the last notification>> A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Maintenance 7.5 Hours | #REF! | 7.5 Hours
QLD | Powerlink | 2023-02-10 08:00 | 2023-02-10 16:00 | Broadsound - Nebo (834) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  | T |  |  | QLD Maintenance 8 Hours | #REF! | 8 Hours
QLD | Powerlink | 2023-02-21 08:00 | 2023-02-21 17:00 | Nebo - Strathmore (8845) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT |  |  | T |  |  | QLD Maintenance 9 Hours | #REF! | 9 Hours
TAS | TasNetworks | 2023-03-02 14:00 | 2023-03-02 15:00 | Gordon - Chapel St No.1 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 30 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Commissioning 60 Minutes | #REF! | 60 Minutes
QLD | Powerlink | 2023-03-06 17:01 | 2023-04-20 17:00 | Strathmore No.1 275/132 kV Transformer | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: NA-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  | T |  |  | QLD Commissioning 45 Days | #REF! | 45 Days
TAS | TasNetworks | 2023-03-07 07:00 | 2023-03-07 14:30 | Gordon - Chapel St No.1 220 kV Line | <<NEW since the last notification>> A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Maintenance 7.5 Hours | #REF! | 7.5 Hours
TAS | TasNetworks | 2023-03-07 09:00 | 2023-03-07 14:00 | Gordon - Chapel St No.2 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Maintenance 5 Hours | #REF! | 5 Hours
TAS | TasNetworks | 2023-03-08 07:00 | 2023-03-08 15:00 | Gordon - Chapel St No.2 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Maintenance 8 Hours | #REF! | 8 Hours
TAS | TasNetworks | 2023-03-09 07:00 | 2023-03-09 14:00 | Gordon - Chapel St No.2 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Maintenance 7 Hours | #REF! | 7 Hours
VIC | AusNet | 2023-03-18 05:00 | 2023-03-21 17:00 | Keilor - South Morang 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 3.5 Days | #REF! | 3.5 Days
QLD | Powerlink | 2023-03-20 08:00 | 2023-03-24 16:00 | Strathmore - Ross (8858) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 72 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 4.3 Days | #REF! | 4.3 Days
VIC | AusNet | 2023-03-22 05:00 | 2023-03-22 17:00 | Keilor - South Morang 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2023-03-23 05:00 | 2023-03-23 17:00 | Keilor - South Morang 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2023-03-24 05:00 | 2023-03-24 17:00 | Keilor - South Morang 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2023-03-25 05:00 | 2023-03-25 17:00 | Keilor - South Morang 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
QLD | Powerlink | 2023-03-28 07:00 | 2023-03-31 16:00 | Ross No.3 288/138/19 kV Transformer | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 8 hrs-Night: 16 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | Commissioning 3.4 Days | #REF! | 3.4 Days
QLD | Powerlink | 2023-04-04 07:00 | 2023-04-05 17:00 | Bouldercombe - Nebo (821) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 6 hrs-Night: 8 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  | T |  |  | QLD Commissioning 1.4 Days | #REF! | 1.4 Days
QLD | Powerlink | 2023-04-06 08:00 | 2023-04-06 16:00 | Nebo - Broadsound (8846) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 1 hr-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 8 Hours | #REF! | 8 Hours
VIC | AusNet | 2023-04-12 06:30 | 2023-04-12 17:00 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10.5 Hours | #REF! | 10.5 Hours
VIC | AusNet | 2023-04-17 07:00 | 2023-04-17 17:00 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #REF! | 10 Hours
QLD | Powerlink | 2023-04-17 07:00 | 2023-04-17 16:00 | Stanwell - Broadsound (856) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may result in shedding Far North QLD load and Lilyvale local load. Following a credible contingency market intervention through issuing of directions may be required. If market intervention is unsuccessful all of North QLD load would be in a credible risk | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 9 Hours | #REF! | 9 Hours
QLD | Powerlink | 2023-04-18 07:00 | 2023-04-18 16:00 | Stanwell - Broadsound (856) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may result in shedding Far North QLD load and Lilyvale local load. Following a credible contingency market intervention through issuing of directions may be required. If market intervention is unsuccessful all of North QLD load would be in a credible risk | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 9 Hours | #REF! | 9 Hours
QLD | Powerlink | 2023-04-19 07:00 | 2023-04-19 16:00 | Stanwell - Broadsound (856) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may result in shedding Far North QLD load and Lilyvale local load. Following a credible contingency market intervention through issuing of directions may be required. If market intervention is unsuccessful all of North QLD load would be in a credible risk | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 9 Hours | #REF! | 9 Hours
QLD | Powerlink | 2023-04-20 07:00 | 2023-04-20 16:00 | Stanwell - Broadsound (856) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may result in shedding Far North QLD load and Lilyvale local load. Following a credible contingency market intervention through issuing of directions may be required. If market intervention is unsuccessful all of North QLD load would be in a credible risk | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 9 Hours | #REF! | 9 Hours
TAS | TasNetworks | 2023-04-20 09:00 | 2023-04-20 16:00 | Gordon - Chapel St No.2 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Maintenance 7 Hours | #REF! | 7 Hours
QLD | Powerlink | 2023-04-21 07:00 | 2023-04-21 16:00 | Stanwell - Broadsound (856) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may result in shedding Far North QLD load and Lilyvale local load. Following a credible contingency market intervention through issuing of directions may be required. If market intervention is unsuccessful all of North QLD load would be in a credible risk | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 9 Hours | #REF! | 9 Hours
QLD | Powerlink | 2023-04-22 07:00 | 2023-04-22 16:00 | Stanwell - Broadsound (856) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may result in shedding Far North QLD load and Lilyvale local load. Following a credible contingency market intervention through issuing of directions may be required. If market intervention is unsuccessful all of North QLD load would be in a credible risk | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 9 Hours | #REF! | 9 Hours
QLD | Powerlink | 2023-04-23 07:00 | 2023-04-23 16:00 | Stanwell - Broadsound (856) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may result in shedding Far North QLD load and Lilyvale local load. Following a credible contingency market intervention through issuing of directions may be required. If market intervention is unsuccessful all of North QLD load would be in a credible risk | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 9 Hours | #REF! | 9 Hours
QLD | Powerlink | 2023-04-24 07:00 | 2023-04-24 16:00 | Stanwell - Broadsound (856) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may result in shedding Far North QLD load and Lilyvale local load. Following a credible contingency market intervention through issuing of directions may be required. If market intervention is unsuccessful all of North QLD load would be in a credible risk | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 9 Hours | #REF! | 9 Hours
QLD | Powerlink | 2023-04-26 07:00 | 2023-04-26 16:00 | Stanwell - Broadsound (856) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may result in shedding Far North QLD load and Lilyvale local load. Following a credible contingency market intervention through issuing of directions may be required. If market intervention is unsuccessful all of North QLD load would be in a credible risk | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 9 Hours | #REF! | 9 Hours
VIC | AusNet | 2023-04-27 06:00 | 2023-04-27 18:30 | Heywood - Tarrone 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | VIC Maintenance 12.5 Hours | #REF! | 12.5 Hours
QLD | Powerlink | 2023-04-27 07:00 | 2023-04-27 16:00 | Stanwell - Broadsound (856) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may result in shedding Far North QLD load and Lilyvale local load. Following a credible contingency market intervention through issuing of directions may be required. If market intervention is unsuccessful all of North QLD load would be in a credible risk | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 9 Hours | #REF! | 9 Hours
VIC | AusNet | 2023-04-28 06:00 | 2023-04-28 18:30 | Heywood - Tarrone 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | VIC Maintenance 12.5 Hours | #REF! | 12.5 Hours
VIC | AusNet | 2023-04-29 06:00 | 2023-04-29 18:30 | Heywood - Tarrone 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | VIC Maintenance 12.5 Hours | #REF! | 12.5 Hours
TAS | TasNetworks | 2023-05-03 15:00 | 2023-05-03 16:00 | Gordon - Chapel St No.2 220 kV Line | <<NEW since the last notification>> A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 1 hr-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Commissioning 60 Minutes | #REF! | 60 Minutes
VIC | AusNet | 2023-05-09 06:00 | 2023-05-09 18:30 | Heywood - Tarrone 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | VIC Maintenance 12.5 Hours | #REF! | 12.5 Hours
QLD | Powerlink | 2023-05-09 07:00 | 2023-06-09 17:00 | Nebo - Strathmore (878) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: NA-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T |  | QLD Commissioning 31.4 Days | #REF! | 31.4 Days
VIC | AusNet | 2023-05-10 06:00 | 2023-05-10 18:30 | Heywood - Tarrone 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | VIC Maintenance 12.5 Hours | #REF! | 12.5 Hours
VIC | AusNet | 2023-05-11 06:00 | 2023-05-11 18:30 | Heywood - Tarrone 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | VIC Maintenance 12.5 Hours | #REF! | 12.5 Hours
QLD | Powerlink | 2023-05-14 08:30 | 2023-05-19 16:00 | Ross No.2 288/138/19 kV Transformer | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 4 hrs-Night: 7 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  | T |  |  | QLD Maintenance 5.3 Days | #REF! | 5.3 Days
VIC | AusNet | 2023-05-15 07:00 | 2023-05-15 17:00 | Hazelwood - Loy Yang Power Station No.2 500 kV Line | A credible contingency event during this planned outage could cause: • A large reduction in generation in Victoria • Load shedding in Victoria | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2023-05-16 06:00 | 2023-05-18 18:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 0 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 2.5 Days | #REF! | 2.5 Days
VIC | AusNet | 2023-05-16 07:00 | 2023-05-16 17:00 | Hazelwood - Loy Yang Power Station No.2 500 kV Line | A credible contingency event during this planned outage could cause: • A large reduction in generation in Victoria • Load shedding in Victoria | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2023-05-17 07:00 | 2023-05-17 17:00 | Hazelwood - Loy Yang Power Station No.1 500 kV Line | A credible contingency event during this planned outage could cause: • A large reduction in generation in Victoria • Load shedding in Victoria | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2023-05-18 07:00 | 2023-05-18 17:00 | Hazelwood - Loy Yang Power Station No.1 500 kV Line | A credible contingency event during this planned outage could cause: • A large reduction in generation in Victoria • Load shedding in Victoria | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
NSW | Transgrid | 2023-05-19 07:00 | 2023-05-21 17:00 | Jindera - Wagga (62) 330 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 6 hrs-Night: 6 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | NSW/ VIC Commissioning 2.4 Days | #REF! | 2.4 Days
VIC | AusNet | 2023-05-23 06:00 | 2023-05-23 18:30 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12.5 Hours | #REF! | 12.5 Hours
VIC | AusNet | 2023-05-24 06:00 | 2023-05-24 18:30 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12.5 Hours | #REF! | 12.5 Hours
VIC | AusNet | 2023-05-24 06:30 | 2023-05-24 17:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10.5 Hours | #REF! | 10.5 Hours
VIC | AusNet | 2023-05-25 06:00 | 2023-05-25 18:30 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12.5 Hours | #REF! | 12.5 Hours
VIC | AusNet | 2023-05-25 06:30 | 2023-05-25 17:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10.5 Hours | #REF! | 10.5 Hours
VIC | AusNet | 2023-05-26 06:00 | 2023-05-26 18:30 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12.5 Hours | #REF! | 12.5 Hours
QLD | Powerlink | 2023-05-26 16:01 | 2023-06-09 07:59 | Ross No.3 288/138/19 kV Transformer | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 0 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 13.7 Days | #REF! | 13.7 Days
VIC | AusNet | 2023-05-29 07:00 | 2023-05-29 17:00 | Ballarat - Waubra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
SA | ElectraNet | 2023-05-29 08:30 | 2023-06-19 17:30 | Cherry Gardens - Tailem Bend 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 16 hrs-Night: 24 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 21.4 Days | #REF! | 21.4 Days
TAS | TasNetworks | 2023-05-31 08:30 | 2023-05-31 16:20 | Gordon - Chapel St No.1 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Maintenance 7.8 Hours | #REF! | 7.8 Hours
SA | ElectraNet | 2023-06-01 08:00 | 2023-06-05 08:00 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 159 hrs-Night: 159 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Commissioning 4 Days | #REF! | 4 Days
TAS | TasNetworks | 2023-06-01 08:30 | 2023-06-01 16:20 | Gordon - Chapel St No.1 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Maintenance 7.8 Hours | #REF! | 7.8 Hours
SA | ElectraNet | 2023-06-05 08:00 | 2023-06-07 13:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 159 hrs-Night: 159 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Commissioning 2.2 Days | #REF! | 2.2 Days
VIC | AusNet | 2023-06-06 06:00 | 2023-06-08 18:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 0 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 2.5 Days | #REF! | 2.5 Days
QLD | Powerlink | 2023-06-09 08:00 | 2023-06-09 16:00 | Strathmore - Ross (8858) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 72 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 8 Hours | #REF! | 8 Hours
QLD | Powerlink | 2023-06-09 08:00 | 2023-06-20 16:00 | Ross No.3 288/138/19 kV Transformer | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 0 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 11.3 Days | #REF! | 11.3 Days
VIC | AusNet | 2023-06-12 06:00 | 2023-06-12 18:30 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12.5 Hours | #REF! | 12.5 Hours
VIC | AusNet | 2023-06-13 06:00 | 2023-06-13 18:30 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12.5 Hours | #REF! | 12.5 Hours
VIC | AusNet | 2023-06-14 06:00 | 2023-06-14 18:30 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12.5 Hours | #REF! | 12.5 Hours
VIC | AusNet | 2023-06-15 06:00 | 2023-06-15 18:30 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12.5 Hours | #REF! | 12.5 Hours
VIC | AusNet | 2023-06-16 06:00 | 2023-06-16 18:30 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12.5 Hours | #REF! | 12.5 Hours
QLD | Powerlink | 2023-06-20 16:01 | 2023-09-18 08:00 | Ross No.3 288/138/19 kV Transformer | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 0 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 89.7 Days | #REF! | 89.7 Days
TAS | TasNetworks | 2023-06-21 15:00 | 2023-06-21 16:30 | Gordon - Chapel St No.1 220 kV Line | <<NEW since the last notification>> A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 1 hr-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Maintenance 1.5 Hours | #REF! | 1.5 Hours
TAS | TasNetworks | 2023-07-04 15:00 | 2023-07-04 16:30 | Gordon - Chapel St No.2 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 1 hr-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Commissioning 1.5 Hours | #REF! | 1.5 Hours
SA | ElectraNet | 2023-07-19 09:00 | 2023-07-21 16:30 | Tailem Bend - Tungkillo 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 48 hrs-Night: 48 hrs | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | SA Maintenance 2.3 Days | #REF! | 2.3 Days
SA | ElectraNet | 2023-07-21 16:30 | 2023-07-23 16:30 | Tailem Bend - Tungkillo 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 48 hrs-Night: 48 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 2 Days | #REF! | 2 Days
SA | ElectraNet | 2023-07-30 05:30 | 2023-07-30 11:00 | Tailem Bend - Tungkillo 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 48 hrs-Night: 48 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 5.5 Hours | #REF! | 5.5 Hours
QLD | Powerlink | 2023-07-31 08:00 | 2023-08-18 16:00 | Strathmore - Ross (8858) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 72 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 18.3 Days | #REF! | 18.3 Days
VIC | AusNet | 2023-08-08 06:30 | 2023-08-08 17:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10.5 Hours | #REF! | 10.5 Hours
QLD | Powerlink | 2023-09-04 07:00 | 2023-10-11 17:00 | Bouldercombe - Nebo (821) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: NA-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 37.4 Days | #REF! | 37.4 Days
QLD | Powerlink | 2023-09-18 08:01 | 2023-12-15 16:00 | Ross No.3 288/138/19 kV Transformer | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 0 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 88.3 Days | #REF! | 88.3 Days
TAS | TasNetworks | 2023-09-27 07:00 | 2023-09-27 16:00 | Gordon - Chapel St No.1 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Maintenance 9 Hours | #REF! | 9 Hours
TAS | TasNetworks | 2023-10-02 07:00 | 2023-10-02 15:00 | Gordon - Chapel St No.2 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Maintenance 8 Hours | #REF! | 8 Hours
QLD | Powerlink | 2023-12-15 16:01 | 2024-02-09 16:00 | Ross No.3 288/138/19 kV Transformer | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 0 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 56 Days | #REF! | 56 Days
QLD | Powerlink | 2024-04-22 08:00 | 2024-07-04 17:00 | Ross No.2 288/138/19 kV Transformer | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 72 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 73.4 Days | #REF! | 73.4 Days
QLD | Powerlink | 2024-07-03 08:00 | 2024-07-16 17:00 | Strathmore - Ross (8858) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 72 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 13.4 Days | #REF! | 13.4 Days
QLD | Powerlink | 2024-10-09 07:00 | 2024-10-21 17:00 | Strathmore - Ross (8858) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 72 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 12.4 Days | #REF! | 12.4 Days
QLD | Powerlink | 2025-04-23 08:00 | 2025-05-09 17:00 | Strathmore - Ross (8858) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 72 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 16.4 Days | #REF! | 16.4 Days
QLD | Powerlink | 2025-04-23 08:00 | 2025-09-05 17:00 | Ross No.3 288/138/19 kV Transformer | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: NA-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 135.4 Days | #REF! | 135.4 Days
QLD | Powerlink | 2025-04-23 08:00 | 2025-09-15 17:00 | Ross No.3 288/138/19 kV Transformer | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: NA-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 145.4 Days | #REF! | 145.4 Days
QLD | Powerlink | 2025-09-02 08:00 | 2025-09-15 17:00 | Strathmore - Ross (8858) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: NA-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 13.4 Days | #REF! | 13.4 Days